## MASTER
GENERAL | [13 empty] | FAILURE RATE NORMAL | [7 empty] | FAILURE RATE PVST
ITEM | ITEM | VERSION | MANUFACTURER | MODEL | ACTUATOR TYPE | ACTUATOR ACTION | ARCHITECTURE TYPE | ASSESSMENT | DATA SOURCE | USEFUL LIFE | REMARKS | HARDWARE FAULT TOLERANCE | SIL CAPABILITY | FAIL DANGEROUS DETECTED | FAIL DANGEROUS UNDETECTED | FAIL SAFE DETECTED | FAIL SAFE UNDETECTED | FAIL ANNUNCIATION DETECTED | FAIL ANNUNCIATION UNDETECTED | FAIL No EFFECT | SFF (%) | FAIL DANGEROUS DETECTED | FAIL DANGEROUS UNDETECTED | FAIL SAFE DETECTED | FAIL SAFE UNDETECTED | FAIL ANNUNCIATION DETECTED | FAIL ANNUNCIATION UNDETECTED | FAIL No EFFECT | SFF (%)
1 | test | 2008.3.01 | AUMA Riester GmbH & CO. KG | SA 1110FC3-F18E1. open/close duty. alarm K1 | Electric | Multi-turn, motor-driven | B | FMEDA | FMEDA by exida | 10 years | None | 0 | 2 | 176 | 488 | 0 | 34 | 114 | 0 | 652 | 66.7 | 613 | 61 | 0 | 34 | 0 | 0 | 656 | 95.5
2 | Test 1 | 2008.3.01 | AUMA Riester GmbH & CO. KG | SA 1110KC3—F18E1. open/close duty. alarm K1 | Electric | Multi-turn, motor-driven | A | FMEDA | FMEDA by exida | 10 years | None | 1 | N/A | 176 | 519 | 0 | 22 | 114 | 2 | 665 | 65.7 | 634 | 61 | 0 | 21 | 0 | 0 | 660 | 95