## Equipment
ID | ITEM | VERSION | MANUFACTURER | MODEL | MEASUREMENT TYPE | ANALOG/ DIGITAL | ARCHITECTURE TYPE | ASSESSMENT | DATA SOURCE | USEFUL LIFE | REMARKS | HARDWARE FAULT TOLERANCE | SIL CAPABILITY | FAIL Low | FAIL HIGH | FAIL DETECTED | FAIL DANGEROUS DETECTED | FAIL DANGEROUS UNDETECTED | FAIL SAFE DETECTED | FAIL SAFE UNDETECTED | FAIL ANNUNCIATION DETECTED | FAIL ANNUNCIATION UNDETECTED | FAIL No EFFECT
1 | test | 2015.1.03 | Daily Thermetrics Corporation | Cattracker, no out-of-range detection | T/C | Analog | A | IEC 61508 Certification | FMEDA by exida | 10 | Single probe, paired with a single pair of connectors and a single thermocouple._x000D_ Thermocouple circuit is such that an open circuit causes the transmitter signal to go out of range. | 0 | 3 | 0 | 0 | 0 | 0 | 1040 | 0 | 0 |  |  | 26
2 | Test 1 | 2011.3.02 | Generic Equipment |  | 2/3-Wire RTD | Analog | A | N/A | exida Comprehensive Analysis | 10 | None | 0 | N/A | 1000 | 600 | 0 | 0 | 400 | 0 | 0
3 | Test 2 | 2011.3.02 | Generic Equipment |  | 4-Wire RTD | Analog | A | N/A | exida Comprehensive Analysis | 10 | None | 0 | N/A | 1400 | 580 | 0 | 0 | 200 | 0 | 0
4 | Test 3 | 2011.3.02 | Generic Equipment |  | Temperature | Analog | A | N/A | exida Comprehensive Analysis | 10 | None | 0 | N/A | 4750 | 0 | 0 | 0 | 250 | 0 | 0
5 | Test 4 | 2012.4.02 | Honeywell Field Products | 1 Remote seal for SmartLine ST700 - HART | Pressure | N/A | A | IEC 61508 Certification | FMEDA by exida | 10 | None | 0 | 3 | 0 | 0 | 0 | 0 | 76 | 0 | 0 |  |  | 19
6 | Test 5 | 2014.3.02 | Net Safety Monitoring, Inc. | ST3 SC311CE Toxic Gas Sensor | Fire & Gas | N/A | B | FMEDA | FMEDA by exida | 2 | The sensor is used in an environment in which the target gas is normally not present. | 0 | N/A | 0 | 0 | 0 | 216 | 47 | 312 | 43 |  |  | 231